## 1-1-1
CONTAM 3.0 |  |  |  |  | AIRNET
Pbar | 101325 | Pa |  |  | Pbar | 101325 | Pa
Tn | 20 | C |  |  | Tn | 20 | C
| 293.15 | K |  |  |  | 293.15 | K
rn | 1.2041 | kg/m3 |  |  | rn | 1.2042 | kg/m3
m | 1.8162e-05 | kg/m-s |  |  | m | 1.8109e-05 | kg/m-s
Re-transition | 100 |  |  |  |  | 100
| path1 | path2 | path3 |  |  | path1 | path2 | path3
Mult |  | 1
D | 0.011284 | 0.011284 | 0.011284 | m | D | 0.01 | 0.01 | 0.01 | m
A | 0.0001 | 0.0001 | 0.0001 | m2 | A | 0.0001 | 0.0001 | 0.0001 | m2
Cd | 0.6 | 0.6 | 0.6 |  | Cd | 0.6 | 0.6 | 0.6
w-trans | 1.6096e-05 | 1.6096e-05 | 1.6096e-05 | kg/s | w-trans | 1.8109e-05 | 1.8109e-05 | 1.8109e-05 | kg/s
Ct | 8.4853e-05 | 8.4853e-05 | 8.4853e-05 |  | Ct | 8.4853e-05 | 8.4853e-05 | 8.4853e-05
K | 8.1243e-09 | 8.1243e-09 | 8.1243e-09 |  | K | 7.2e-09 | 7.2e-09 | 7.2e-09
Ce | 4.899e-05 |  |  |  | Ce | 4.899e-05
Ke | 2.7081e-09 |  |  |  | Ke | 2.4e-09
w-turb | 5.3757e-05 | x sqrt(DP) |  |  | w-turb | 5.3758e-05 | x sqrt(DP)
w-lam | 0.00017954 | x DP |  |  | w-lam | 0.00015959 | x DP
dP-trans | 0.029885 | 0.029885 | 0.029885 |  | dP-trans | 0.037824 | 0.037824 | 0.037824
dP-lam-all | 0.089654 | Pa |  |  | dP-lam-all | 0.11347 | Pa
dP-turb-all | 0.089654 | Pa |  |  | dP-turb-all | 0.11347 | Pa
CONTAM should match green values |  |  |  |  | AIRNET matched these green values
DP14 | w-turb | w-lam |  |  | DP14 | w-turb | w-lam
100 | 0.00053757 | 0.017954 |  |  | 100 | 0.00053758 | 0.015959
| flow1 | flow2 | flow3 |  |  | flow1 | flow2 | flow3
| turbulent | turbulent | turbulent |  |  | turbulent | turbulent | turbulent
Note on B13: All path1 and path3 values on the "1-#-1" sheets reference this one. You only need to change this one and all will change. Set to 0.0001 for first set and 0.001 for second set as described in the AIRNET documentation. Use the BASE sheet for more generic cases.

## 1-2-1
CONTAM 3.0 |  |  |  |  | OLD AIRNET
Pbar | 101325 | Pa |  |  | Pbar | 101325 | Pa
Tn | 20 | C |  |  | Tn | 20 | C
| 293.15 | K |  |  |  | 293.15 | K
rn | 1.2041 | kg/m3 |  |  | rn | 1.2042 | kg/m3
m | 1.8162e-05 | kg/m-s |  |  | m | 1.8109e-05 | kg/m-s
Re-transition | 100 |  |  |  |  | 100
| path1 | path2 | path3 |  |  | path1 | path2 | path3
Mult |  | 10
D | 0.011284 | 0.035682 | 0.011284 | m | D | 0.01 | 0.031623 | 0.01 | m
A | 0.0001 | 0.001 | 0.0001 | m2 | A | 0.0001 | 0.001 | 0.0001 | m2
Cd | 0.6 | 0.6 | 0.6 |  | Cd | 0.6 | 0.6 | 0.6
w-trans | 1.6096e-05 | 5.09e-05 | 1.6096e-05 | kg/s | w-trans | 1.8109e-05 | 5.7265e-05 | 1.8109e-05 | kg/s
Ct | 8.4853e-05 | 0.00084853 | 8.4853e-05 |  | Ct | 8.4853e-05 | 0.00084853 | 8.4853e-05
K | 8.1243e-09 | 2.5691e-07 | 8.1243e-09 |  | K | 7.2e-09 | 2.2768e-07 | 7.2e-09
Ce | 5.9851e-05 |  |  |  | Ce | 5.9851e-05
Ke | 3.9989e-09 |  |  |  | Ke | 3.544e-09
w-turb | 6.5675e-05 | x sqrt(DP) |  |  | w-turb | 6.5676e-05 | x sqrt(DP)
w-lam | 0.00026511 | x DP |  |  | w-lam | 0.00023566 | x DP
dP-trans | 0.029885 | 0.0029885 | 0.029885 |  | dP-trans | 0.037824 | 0.0037824 | 0.037824
dP-lam-all | 0.060714 | Pa |  |  | dP-lam-all | 0.076844 | Pa
dP-turb-all | 0.60068 | Pa |  |  | dP-turb-all | 0.76026 | Pa
CONTAM should match green values |  |  |  |  | AIRNET matched these green values
DP14 | w-turb | w-lam |  |  | DP14 | w-turb | w-lam
100 | 0.00065675 | 0.026511 |  |  | 100 | 0.00065676 | 0.023566
| flow1 | flow2 | flow3 |  |  | flow1 | flow2 | flow3
| turbulent | turbulent | turbulent |  |  | turbulent | turbulent | turbulent

## 1-3-1
CONTAM 3.0 |  |  |  |  | OLD AIRNET
Pbar | 101325 | Pa |  |  | Pbar | 101325 | Pa
Tn | 20 | C |  |  | Tn | 20 | C
| 293.15 | K |  |  |  | 293.15 | K
rn | 1.2041 | kg/m3 |  |  | rn | 1.2042 | kg/m3
m | 1.8162e-05 | kg/m-s |  |  | m | 1.8109e-05 | kg/m-s
Re-transition | 100 |  |  |  |  | 100
| path1 | path2 | path3 |  |  | path1 | path2 | path3
Mult |  | 100
D | 0.011284 | 0.11284 | 0.011284 | m | D | 0.01 | 0.1 | 0.01 | m
A | 0.0001 | 0.01 | 0.0001 | m2 | A | 0.0001 | 0.01 | 0.0001 | m2
Cd | 0.6 | 0.6 | 0.6 |  | Cd | 0.6 | 0.6 | 0.6
w-trans | 1.6096e-05 | 0.00016096 | 1.6096e-05 | kg/s | w-trans | 1.8109e-05 | 0.00018109 | 1.8109e-05 | kg/s
Ct | 8.4853e-05 | 0.0084853 | 8.4853e-05 |  | Ct | 8.4853e-05 | 0.0084853 | 8.4853e-05
K | 8.1243e-09 | 8.1243e-06 | 8.1243e-09 |  | K | 7.2e-09 | 7.2e-06 | 7.2e-09
Ce | 5.9999e-05 |  |  |  | Ce | 5.9999e-05
Ke | 4.0601e-09 |  |  |  | Ke | 3.5982e-09
w-turb | 6.5837e-05 | x sqrt(DP) |  |  | w-turb | 6.5839e-05 | x sqrt(DP)
w-lam | 0.00026917 | x DP |  |  | w-lam | 0.00023926 | x DP
dP-trans | 0.029885 | 0.00029885 | 0.029885 |  | dP-trans | 0.037824 | 0.00037824 | 0.037824
dP-lam-all | 0.059799 | Pa |  |  | dP-lam-all | 0.075686 | Pa
dP-turb-all | 5.9772 | Pa |  |  | dP-turb-all | 7.5652 | Pa
CONTAM should match green values |  |  |  |  | AIRNET matched these green values
DP14 | w-turb | w-lam |  |  | DP14 | w-turb | w-lam
100 | 0.00065837 | 0.026917 |  |  | 100 | 0.00065839 | 0.023926
| flow1 | flow2 | flow3 |  |  | flow1 | flow2 | flow3
| turbulent | turbulent | turbulent |  |  | turbulent | turbulent | turbulent

## 1-4-1
CONTAM 3.0 |  |  |  |  | OLD AIRNET
Pbar | 101325 | Pa |  |  | Pbar | 101325 | Pa
Tn | 20 | C |  |  | Tn | 20 | C
| 293.15 | K |  |  |  | 293.15 | K
rn | 1.2041 | kg/m3 |  |  | rn | 1.2042 | kg/m3
m | 1.8162e-05 | kg/m-s |  |  | m | 1.8109e-05 | kg/m-s
Re-transition | 100 |  |  |  |  | 100
| path1 | path2 | path3 |  |  | path1 | path2 | path3
Mult |  | 1000
D | 0.011284 | 0.35682 | 0.011284 | m | D | 0.01 | 0.31623 | 0.01 | m
A | 0.0001 | 0.1 | 0.0001 | m2 | A | 0.0001 | 0.1 | 0.0001 | m2
Cd | 0.6 | 0.6 | 0.6 |  | Cd | 0.6 | 0.6 | 0.6
w-trans | 1.6096e-05 | 0.000509 | 1.6096e-05 | kg/s | w-trans | 1.8109e-05 | 0.00057265 | 1.8109e-05 | kg/s
Ct | 8.4853e-05 | 0.084853 | 8.4853e-05 |  | Ct | 8.4853e-05 | 0.084853 | 8.4853e-05
K | 8.1243e-09 | 0.00025691 | 8.1243e-09 |  | K | 7.2e-09 | 0.00022768 | 7.2e-09
Ce | 6e-05 |  |  |  | Ce | 6e-05
Ke | 4.0621e-09 |  |  |  | Ke | 3.5999e-09
w-turb | 6.5839e-05 | x sqrt(DP) |  |  | w-turb | 6.584e-05 | x sqrt(DP)
w-lam | 0.0002693 | x DP |  |  | w-lam | 0.00023938 | x DP
dP-trans | 0.029885 | 2.9885e-05 | 0.029885 |  | dP-trans | 0.037824 | 3.7824e-05 | 0.037824
dP-lam-all | 0.05977 | Pa |  |  | dP-lam-all | 0.075649 | Pa
dP-turb-all | 59.7691 | Pa |  |  | dP-turb-all | 75.6478 | Pa
CONTAM should match green values |  |  |  |  | AIRNET matched these green values
DP14 | w-turb | w-lam |  |  | DP14 | w-turb | w-lam
100 | 0.00065839 | 0.02693 |  |  | 100 | 0.0006584 | 0.023938
| flow1 | flow2 | flow3 |  |  | flow1 | flow2 | flow3
| turbulent | turbulent | turbulent |  |  | turbulent | turbulent | turbulent

## 1-5-1
CONTAM 3.0 |  |  |  |  | OLD AIRNET
Pbar | 101325 | Pa |  |  | Pbar | 101325 | Pa
Tn | 20 | C |  |  | Tn | 20 | C
| 293.15 | K |  |  |  | 293.15 | K
rn | 1.2041 | kg/m3 |  |  | rn | 1.2042 | kg/m3
m | 1.8162e-05 | kg/m-s |  |  | m | 1.8109e-05 | kg/m-s
Re-transition | 100 |  |  |  |  | 100
| path1 | path2 | path3 |  |  | path1 | path2 | path3
Mult |  | 10000
D | 0.011284 | 1.1284 | 0.011284 | m | D | 0.01 | 1 | 0.01 | m
A | 0.0001 | 1 | 0.0001 | m2 | A | 0.0001 | 1 | 0.0001 | m2
Cd | 0.6 | 0.6 | 0.6 |  | Cd | 0.6 | 0.6 | 0.6
w-trans | 1.6096e-05 | 0.0016096 | 1.6096e-05 | kg/s | w-trans | 1.8109e-05 | 0.0018109 | 1.8109e-05 | kg/s
Ct | 8.4853e-05 | 0.84853 | 8.4853e-05 |  | Ct | 8.4853e-05 | 0.84853 | 8.4853e-05
K | 8.1243e-09 | 0.0081243 | 8.1243e-09 |  | K | 7.2e-09 | 0.0072 | 7.2e-09
Ce | 6e-05 |  |  |  | Ce | 6e-05
Ke | 4.0622e-09 |  |  |  | Ke | 3.6e-09
w-turb | 6.5839e-05 | x sqrt(DP) |  |  | w-turb | 6.584e-05 | x sqrt(DP)
w-lam | 0.0002693 | x DP |  |  | w-lam | 0.00023938 | x DP
dP-trans | 0.029885 | 2.9885e-06 | 0.029885 |  | dP-trans | 0.037824 | 3.7824e-06 | 0.037824
dP-lam-all | 0.059769 | Pa |  |  | dP-lam-all | 0.075648 | Pa
dP-turb-all | 597.6908 | Pa |  |  | dP-turb-all | 756.4779 | Pa
CONTAM should match green values |  |  |  |  | AIRNET matched these green values
DP14 | w-turb | w-lam |  |  | DP14 | w-turb | w-lam
100 | 0.00065839 | 0.02693 |  |  | 100 | 0.0006584 | 0.023938
| flow1 | flow2 | flow3 |  |  | flow1 | flow2 | flow3
| turbulent | laminar | turbulent |  |  | turbulent | laminar | turbulent

## 1-6-1
CONTAM 3.0 |  |  |  |  | OLD AIRNET
Pbar | 101325 | Pa |  |  | Pbar | 101325 | Pa
Tn | 20 | C |  |  | Tn | 20 | C
| 293.15 | K |  |  |  | 293.15 | K
rn | 1.2041 | kg/m3 |  |  | rn | 1.2042 | kg/m3
m | 1.8162e-05 | kg/m-s |  |  | m | 1.8109e-05 | kg/m-s
Re-transition | 100 |  |  |  |  | 100
| path1 | path2 | path3 |  |  | path1 | path2 | path3
Mult |  | 100000
D | 0.011284 | 3.5682 | 0.011284 | m | D | 0.01 | 3.1623 | 0.01 | m
A | 0.0001 | 10 | 0.0001 | m2 | A | 0.0001 | 10 | 0.0001 | m2
Cd | 0.6 | 0.6 | 0.6 |  | Cd | 0.6 | 0.6 | 0.6
w-trans | 1.6096e-05 | 0.00509 | 1.6096e-05 | kg/s | w-trans | 1.8109e-05 | 0.0057265 | 1.8109e-05 | kg/s
Ct | 8.4853e-05 | 8.4853 | 8.4853e-05 |  | Ct | 8.4853e-05 | 8.4853 | 8.4853e-05
K | 8.1243e-09 | 0.25691 | 8.1243e-09 |  | K | 7.2e-09 | 0.22768 | 7.2e-09
Ce | 6e-05 |  |  |  | Ce | 6e-05
Ke | 4.0622e-09 |  |  |  | Ke | 3.6e-09
w-turb | 6.5839e-05 | x sqrt(DP) |  |  | w-turb | 6.584e-05 | x sqrt(DP)
w-lam | 0.0002693 | x DP |  |  | w-lam | 0.00023938 | x DP
dP-trans | 0.029885 | 2.9885e-07 | 0.029885 |  | dP-trans | 0.037824 | 3.7824e-07 | 0.037824
dP-lam-all | 0.059769 | Pa |  |  | dP-lam-all | 0.075648 | Pa
dP-turb-all | 5976.9084 | Pa |  |  | dP-turb-all | 7564.7792 | Pa
CONTAM should match green values |  |  |  |  | AIRNET matched these green values
DP14 | w-turb | w-lam |  |  | DP14 | w-turb | w-lam
100 | 0.00065839 | 0.02693 |  |  | 100 | 0.0006584 | 0.023938
| flow1 | flow2 | flow3 |  |  | flow1 | flow2 | flow3
| turbulent | laminar | turbulent |  |  | turbulent | laminar | turbulent

## 1-7-1
CONTAM 3.0 |  |  |  |  | OLD AIRNET
Pbar | 101325 | Pa |  |  | Pbar | 101325 | Pa
Tn | 20 | C |  |  | Tn | 20 | C
| 293.15 | K |  |  |  | 293.15 | K
rn | 1.2041 | kg/m3 |  |  | rn | 1.2042 | kg/m3
m | 1.8162e-05 | kg/m-s |  |  | m | 1.8109e-05 | kg/m-s
Re-transition | 100 |  |  |  |  | 100
| path1 | path2 | path3 |  |  | path1 | path2 | path3
Mult |  | 1000000
D | 0.011284 | 11.2838 | 0.011284 | m | D | 0.01 | 10 | 0.01 | m
A | 0.0001 | 100 | 0.0001 | m2 | A | 0.0001 | 100 | 0.0001 | m2
Cd | 0.6 | 0.6 | 0.6 |  | Cd | 0.6 | 0.6 | 0.6
w-trans | 1.6096e-05 | 0.016096 | 1.6096e-05 | kg/s | w-trans | 1.8109e-05 | 0.018109 | 1.8109e-05 | kg/s
Ct | 8.4853e-05 | 84.8528 | 8.4853e-05 |  | Ct | 8.4853e-05 | 84.8528 | 8.4853e-05
K | 8.1243e-09 | 8.1243 | 8.1243e-09 |  | K | 7.2e-09 | 7.2 | 7.2e-09
Ce | 6e-05 |  |  |  | Ce | 6e-05
Ke | 4.0622e-09 |  |  |  | Ke | 3.6e-09
w-turb | 6.5839e-05 | x sqrt(DP) |  |  | w-turb | 6.584e-05 | x sqrt(DP)
w-lam | 0.0002693 | x DP |  |  | w-lam | 0.00023938 | x DP
dP-trans | 0.029885 | 2.9885e-08 | 0.029885 |  | dP-trans | 0.037824 | 3.7824e-08 | 0.037824
dP-lam-all | 0.059769 | Pa |  |  | dP-lam-all | 0.075648 | Pa
dP-turb-all | 59769.0843 | Pa |  |  | dP-turb-all | 75647.7915 | Pa
CONTAM should match green values |  |  |  |  | AIRNET matched these green values
DP14 | w-turb | w-lam |  |  | DP14 | w-turb | w-lam
100 | 0.00065839 | 0.02693 |  |  | 100 | 0.0006584 | 0.023938
| flow1 | flow2 | flow3 |  |  | flow1 | flow2 | flow3
| turbulent | laminar | turbulent |  |  | turbulent | laminar | turbulent

## BASE
AIRNET Test case - Powerlaw Test #2 |  |  |  | ORIFICE |  | CONTAM 3.0 |  |  |  |  | OLD AIRNET
|  |  |  | For turbulent flow: |  | Pbar | 101325 | Pa |  |  | Pbar | 101325 | Pa
|  |  |  | Q = Cd A sqrt(2 dP / rho) |  | Tn | 20 | C |  |  | Tn | 20 | C
|  |  |  | w = rho Q = Cd A sqrt(2 rho dP) |  |  | 293.15 | K |  |  |  | 293.15 | K
|  |  |  | = C sqrt(rho dP) in general powerlaw form |  | rn | 1.2041 | kg/m3 |  |  | rn | 1.2042 | kg/m3
|  |  |  | where |  | m | 1.8162e-05 | kg/m-s |  |  | m | 1.8109e-05 | kg/m-s
|  |  |  | C = Cd A sqrt(2) |  | Re-transition | 100 |  |  |  |  | 100
Re = ruD/m
|  |  |  | For laminar flow: |  |  | path1 | path2 | path3 |  |  | path1 | path2 | path3
| Pstd | 101325 | Pa | w = rho K dP / mu |  | D | 0.011284 | 0.11284 | 0.011284 | m | D | 0.011284 | 0.11284 | 0.011284 | m
| Tstd | 20 | C |  |  | A | 0.0001 | 0.01 | 0.0001 | m2 | A | 0.0001 | 0.01 | 0.0001 | m2
|  | 293.15 | K | At the Laminar to Turbulent transition Re: |  | Cd | 0.6 | 0.6 | 0.6 |  | Cd | 0.6 | 0.6 | 0.6
| rstd | 1.2041 | kg/m3 | w-turb = w-lam |  | w-trans | 1.6096e-05 | 0.00016096 | 1.6096e-05 | kg/s | w-trans | 1.6049e-05 | 0.00016049 | 1.6049e-05 | kg/s
| Rair | 287.055 | J/kg-K | w = mu A Re/D => Flow is laminar below this |  | Ct | 8.4853e-05 | 0.0084853 | 8.4853e-05 |  | Ct | 8.4853e-05 | 0.0084853 | 8.4853e-05
| m | 1.8162e-05 | kg/m-s |  |  | K | 8.1243e-09 | 8.1243e-06 | 8.1243e-09 |  | K | 8.1243e-09 | 8.1243e-06 | 8.1243e-09
| n | 1.5084e-05 | m2/s |  |  | Ce | 5.9999e-05 |  |  |  | Ce | 5.9999e-05
[6 empty] | Ke | 4.0601e-09 |  |  |  | Ke | 4.0601e-09
[5 empty] | TURB FLOW EQUATION --> | w-turb | 6.5837e-05 | x sqrt(DP) |  |  | w-turb | 6.5839e-05 | x sqrt(DP)
[5 empty] | LAM FLOW EQUATION --> | w-lam | 0.00026917 | x DP |  |  | w-lam | 0.00026998 | x DP
[6 empty] | dP-trans | 0.029885 | 0.00029885 | 0.029885 |  | dP-trans | 0.029707 | 0.00029707 | 0.029707
[6 empty] | dP-lam-all | 0.059799 | Pa |  |  | dP-lam-all | 0.059443 | Pa
[6 empty] | dP-turb-all | 5.9772 | Pa |  |  | dP-turb-all | 5.9417 | Pa
[6 empty] | DP14 | w-turb | w-lam |  |  | DP14 | w-turb | w-lam
[6 empty] | 100 | 0.00065837 | 0.026917 |  |  | 100 | 0.00065839 | 0.026998
[7 empty] | flow1 | flow2 | flow3 |  |  | flow1 | flow2 | flow3
[7 empty] | turbulent | turbulent | turbulent |  |  | turbulent | turbulent | turbulent
path1 path2 path3
|--------------- DP14 = 100 Pa --------------|